{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["技术参数"],"not_rendered":{"images":4},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"技术参数","index":0,"n_rows":40,"n_cols":8,"rows_kept":40,"merged":[[0,0,0,7],[1,0,4,1],[1,3,1,4],[1,5,1,6],[2,3,2,4],[2,5,2,6],[3,3,3,4],[3,5,3,6],[4,3,4,4],[4,5,4,6],[5,0,5,7],[6,0,6,2],[6,3,6,7],[7,2,7,7],[8,0,20,0],[8,1,20,1],[8,2,9,2],[8,3,8,7],[9,3,9,7],[10,2,12,2],[10,3,10,7],[11,3,11,7],[12,3,12,7],[13,3,13,7],[14,3,14,7],[15,3,15,7],[16,3,16,7],[17,3,17,7],[18,3,18,7],[19,3,19,7],[20,3,20,7],[21,1,21,2],[21,3,21,7],[22,1,22,2],[22,3,22,7],[23,1,23,2],[23,3,23,7],[24,0,26,0],[24,1,26,1],[24,3,24,7],[25,3,25,7],[26,3,26,7],[27,1,27,2],[27,3,27,7],[28,0,28,7],[29,1,29,2],[29,3,29,7],[30,1,30,2],[30,3,30,7],[31,1,31,2],[31,3,31,7],[32,1,32,2],[32,3,32,7],[33,1,33,2],[33,3,33,7],[34,1,34,2],[34,3,34,7],[35,0,37,0],[35,1,37,1],[35,3,35,7],[36,3,36,7],[37,3,37,7],[38,0,38,7],[39,0,39,7],[40,0,40,7],[41,0,41,7],[42,0,42,7],[43,0,43,7]],"flags":["formulas_cached_only"]}
["集装箱式建筑技术参数"]
["参数指标",null,"使用年限","20年",null,"风荷载",null,"0.60kN/㎡"]
[null,null,"隔音性能","隔声量≥30dB",null,"防火性能",null,"A 级"]
[null,null,"排水方式","有组织内下水管排水",null,"抗震设防烈度",null,"7度"]
[null,null,"地面活载","2.5kN/㎡",null,"屋面活载",null,"1.0kN/㎡"]
["一  单个集装箱技术参数"]
["中心尺寸（图纸轴线尺寸）：6000mm*3000mm*3000mm",null,null,"技术参数"]
[1,"墙板","75mm厚岩棉彩钢板，双面≧0.40mm彩钢板，岩棉80kg/m³，双面橘皮纹，颜色双白"]
[2,"框架","顶框","顶主梁：钢材，表面镀锌处理，壁厚≧3.0mm"]
[{"$nulls":3},"顶次梁：钢材，表面镀锌处理，壁厚≧1.3mm"]
[null,null,"底框","底主梁：钢材，表面镀锌处理，壁厚≧3.0mm"]
[{"$nulls":3},"底次梁：钢材，表面镀锌处理，壁厚≧1.5mm"]
[{"$nulls":3},"地板：水泥纤维板，厚度≧18mm"]
[null,null,"立柱","立柱：钢材，表面镀锌处理，壁厚≧3.0mm"]
[null,null,"角件","角件：钢材，表面镀锌处理，壁厚≧4.0mm"]
[null,null,"顶板","彩钢板，360度咬合，壁厚≧0.45mm，含丁基胶带防水"]
[null,null,"顶部保温层","75mm厚玻璃棉，铺设PE树脂膜"]
[null,null,"底板","彩钢板，厚度≧0.4mm"]
[null,null,"落水管","PVC落水管，直径≧50mm，四角均设排水管。"]
[null,null,"泛水槽","彩钢板，壁厚≧0.5mm，墙板底部泛水包边一体槽，四角均设排水口。"]
[null,null,"节点表面处理","静电喷塑烤漆处理，厚度≧80μm"]
[3,"门",null,"套装门，尺寸宽840mm×高2035mm，彩钢板壁厚≧0.5mm, 带防火锁。"]
[4,"窗",null,"塑钢推拉窗，尺寸宽925mm*高1100mm，双层玻璃，带纱窗，带防盗功能。"]
[5,"地面装饰",null,"PVC防滑耐磨地板，厚度≧1.6mm，热熔焊缝"]
[6,"内饰","阴角","彩钢板，壁厚≧0.5mm"]
[null,null,"立柱包边","彩钢板，壁厚≧0.5mm"]
[null,null,"踢脚线","PVC材质，棕色"]
[7,"室内电路",null," 灯  具：条形灯×2套，功率≧36W；\n 插  座：三孔（空调）插座1个,五孔插座4个,单开1个\n 电  线：入户4mm2，空调4mm2，插座2.5mm2，照明1.5mm2\n 配电箱：暗装配电箱1个,32A漏保2p1个；\n 进线头：工业进线插座一套\n注：以上材料均必须选用符合国家标准的品牌。"]
["二  其他配置"]
[1,"二楼阳台，平台底座",null,"地板：花纹铝板，厚度≧3.0mm；\n栏杆、扶手：不锈钢，壁厚≧1.0mm。"]
[2,"厨房及餐厅",null,"地板：花纹铝板，厚度≧3.0mm"]
[3,"室内楼梯",null,"楼梯：钢板，厚度≧3.0mm；\n栏杆、扶手：304不锈钢，壁厚≧1.0mm。"]
[4,"玻璃幕墙",null,"龙骨：铝合金，壁厚≧1.5mm；\n玻璃：中空玻璃5+9A+5"]
[5,"钢化玻璃雨棚",null,"龙骨：钢材，壁厚≧3.0mm；\n钢化夹胶玻璃6+6"]
[6,"铝合金手动双开门",null,"龙骨：铝合金，壁厚≧1.5mm；\n玻璃：中空玻璃5+9A+5"]
[7,"卫生间","地板","地板：花纹铝板，厚度≧3.0mm"]
[null,null,"台盆、小便器、蹲便器","必须选用符合国家标准的优质以上品牌"]
[null,null,"冲淋设备","必须选用符合国家标准的优质以上品牌"]
["注：上表中各设备及材料中未明确的参数由供应商根据本项目工程实际情况及磋商文件要求自行选定。"]
["图例\n(仅供参考，具体做法由供应商自定）"]